## Indoor
Technical Specifications
Split-type Inverter
| Sr No | Parameter |  | Unit | Value
61 | 57 | Indoor Unit | Indoor Unit Model | -- | GWH09QB-K3DNA6D/I | GWH12QB-K3DNA6D/I
63 | 58 |  | Fan Type | -- | Cross-flow | Cross-flow
64 | 59 |  | Fan Diameter Length(D×L) | mm | Ф98×580 | Ф98×580
65 | 60 |  | Fan Diameter Length(D×L) | inch | 3 6/7×22 5/6 | 3 6/7×22 5/6
66 | 61 |  | Cooling Speed | r/min | 1300/1200/1050/800 | 1350/1200/1050/750
67 | 62 |  | Heating Speed | r/min | 1300/1200/1050/900 | 1350/1200/1050/850
68 | 63 |  | Fan Motor Power Output | W | 20 | 20
69 | 64 |  | Fan Motor RLA | A | 0.215 | 0.215
70 | 65 |  | Fan Motor Capacitor | μF | 1 | 1
71 | 66 |  | Heater Power Input | W | / | /
76 | 67 |  | Evaporator Form | -- | Aluminum Fin-copper Tube | Aluminum Fin-copper Tube
77 | 68 |  | Evaporator Pipe Diameter | mm | φ5 | φ5
78 | 69 |  | Evaporator Pipe Diameter | inch | 0.286 | 0.286
79 | 70 |  | Evaporator Row-fin Gap | mm | 2-1.4 | 2-1.4
80 | 71 |  | Evaporator Row-fin Gap | inch | 2-1/18 | 2-1/18
81 | 72 |  | Evaporator Coil Length (L×D×W) | mm | 584×22.8×266.7 | 584×22.8×266.7
82 | 73 |  | Evaporator Coil Length (L×D×W) | inch | 23×7/8×10 8/16 | 23×7/8×10 8/16
83 | 74 |  | Swing Motor Model | -- | MP24AA | MP24AA
84 | 75 |  | Swing Motor Power Output | W | 1.5 | 1.5
85 | 76 |  | Fuse Current | A | 3.15 | 3.15
86 | 77 |  | Set Temperature Range | ℃ | 16～30 | 16～30
87 | 78 |  | Set Temperature Range | ℉ | 61～86 | 61～86
91/92/93/94/95/96/97 | 79 |  | Sound Pressure Level | dB (A) | 40/36/34/29 | 42/37/34/28
98/99/100/101/102/103/104 | 80 |  | Sound Power Level | dB (A) | 50/47/44/39 | 55/47/44/38
105×107×109 | 81 |  | Dimension (W×H×D) | mm | 790×275×200 | 790×275×200
106×108×110 | 82 |  | Dimension (W×H×D) | inch | 31.102×10.827×7.874 | 31.102×10.827×7.874
111×113×115 | 83 |  | Dimension of Carton Box (L×W×H) | mm | 850×339×262 | 850×339×262
112×114×116 | 84 |  | Dimension of Carton Box (L×W×H) | inch | 33.464×13.346×10.315 | 33.464×13.346×10.315
117×119×121 | 85 |  | Dimension of Package(L×W×H) | mm | 852×355×273 | 852×355×273
118×120×122 | 86 |  | Dimension of Package(L×W×H) | inch | 33.543×13.976×10.748 | 33.543×13.976×10.748
130 | 87 |  | Stacked Layers | － | 7 | 7
123 | 88 |  | Net Weight | kg | 9 | 9
124 | 89 |  | Net Weight | lb | 19.8 | 19.8
125 | 90 |  | Gross Weight | kg | 11 | 11
126 | 91 |  | Gross Weight | lb | 24.3 | 24.3

## Outdoor
Technical Specifications
Split Air Conditioner Outdoor Unit
Sr No | Parameter | Unit | Value
1 | Model | － | GWHD<18>NK3KO | GWHD<21>NK3KO | GWHD<28>NK3KO
2 | Product Code | － | CB228W06300 | CB228W06400 | CB228W06201
3 | Cooling Capacity | kW | 5.20 | 6.10 | 8.00
4 | Cooling Capacity | Btu/h | 17742.4 | 20813.2 | 27296
5 | Min. Cooling Capacity | W | 2139.508 | 2198.124 | 2286
6 | Min. Cooling Capacity | Btu/h | 7300 | 7500 | 7800
7 | Max. Cooling Capacity | W | 5800 | 7327.081 | 10258
8 | Max. Cooling Capacity | Btu/h | 19800 | 25000 | 35000
9 | Heating Capacity | kW | 5.40 | 6.50 | 9.30
10 | Heating Capacity | Btu/h | 18424.8 | 22178 | 31731.6
11 | Min. Heating Capacity | W | 2579.132 | 3604.924 | 3664
12 | Min. Heating Capacity | Btu/h | 8800 | 12300 | 12500
13 | Max. Heating Capacity | W | 5920.281 | 8499.414 | 10258
14 | Max. Heating Capacity | Btu/h | 20200 | 29000 | 35000
15 | EER | W/W | 3.586 | 3.194 | 3.15
16 | EER | (Btu/h)/W | 12.236 | 10.897 | 10.75
17 | COP | W/W | 3.724 | 3.757 | 3.73
18 | COP | (Btu/h)/W | 12.707 | 12.82 | 12.74
19 | SEER | － | 6.30 | 6.10 | 6.10
20 | Air Flow Volume | m3/h | 3200 | 3200 | 4000
21 | Air Flow Volume | CFM | 1883.2 | 1883.2 | 2354
22 | Sound Pressure Level | dB(A) | 56 | 56 | 58
23 | Sound Power Level | dB(A) | 62 | 65 | 65
24 | Rated Voltage | V | 220-240 | 220-240 | 220-240
25 | Rated Frequency | Hz | 50 | 50 | 50
26 | Phases | － | 1 | 1 | 1
27 | Cross-sectional Area of Power Cable Conductor | mm2 | 1.00 | 2.50 | 2.50
28 | Recommended Power Cable(Core) | N | 3 | 3 | 3
29 | Fuse Current | A | 25 | 30 | 30
30 | Cooling Power Input | kW | 1.45 | 1.91 | 2.54
31 | Heating Power Input | kW | 1.45 | 1.73 | 2.49
32 | Rated Power Input | kW | 1.78 | 2.87 | 3.58
33 | Cooling Current Input | A | 6.433 | 8.474 | 11.27
34 | Heating Current Input | A | 6.433 | 7.675 | 11.05
35 | Rated Current | A | 7.897 | 12.733 | 15.88
36 | Starting Current | A | 5 | 5 | 5
37 | Compressor Trademark | － | GREE | GREE | GREE
38 | Compressor Manufacturer | － | ZHUHAI LANDA COMPRESSOR CO.,LTD | ZHUHAI LANDA COMPRESSOR CO.,LTD | ZHUHAI LANDA COMPRESSOR CO.,LTD
39 | Compressor Model1 | － | QXA-B141zF030A | QXAS-D23zX090B | QXAS-D23zX090B
40 | Compressor Type1 | － | Inverter Rotary | Inverter Rotary | Inverter Rotary
41 | Compressor Capacity | W | 4225 | 7150 | 7150
42 | Compressor Power Input | W | 1440 | 2550 | 2550
43 | Compressor Rated Load Amp (RLA) | A | 7.2 | 11.5 | 11.5
44 | Compressor Locked Rotor Amp (L.R.A) | A | 25 | 40 | 40
45 | Compressor Thermal Protector | － | 1NT11L-6233 KSD115℃ HPC115/95U1 | 1NT11L-6233 KSD115℃ HPC 115/ 95 | 1NT11L-6233 KSD115℃ HPC 115/ 95
46 | Compressor Crankcase | W | 25 | 25 | 25
47 | Compressor Refrigerant Oil Type | － | RB68EP | RB68EP | RB68EP
48 | Compressor Refrigerant Oil Charge Volume | L | 0.405 | 0.950 | 0.950
49 | Chassis Electrical Heater Power Input | W | 96 | 96 | /
51 | Fan Type | － | Axial-flow | Axial-flow | Axial-flow
52 | Fan Quantity | － | 1 | 1 | 1
53 | Fan Diameter-height | mm | 520-154 | 520-154 | 550-120
54 | Motor Model | － | LW60M-ZL | LW60M-ZL | LW92K-ZL
55 | Motor Type | － | DC motor | DC motor | DC motor
56 | Motor Insulation Class | － | E | E | E
57 | Motor Safe Class | － | IP24 | IP24 | IP24
59 | Motor Full Load Amp(FLA) | A | 0.426 | 0.426 | 0.486
60 | Fan Motor Drive Type | － | Direct drive | Direct drive | Direct drive
61 | Fan Motor Speed | rpm | 800 | 800 | 800
62 | Fan Motor Power Output | W | 60 | 60 | 90
65 | Condenser Material | － | Aluminum Fin-copper Tube | Aluminum Fin-copper Tube | Aluminum Fin-copper Tube
66 | Condenser Face Area | m2 | 0.56 | 0.56 | 0.73
67 | Condenser Pipe Diameter | mm | φ7 | φ9.52 | φ7
68 | Condenser Number of Rows | － | 2 | 2 | 2
69 | Condenser Tube Pitch(a)×Row Pitch(b) | mm | 19.05×22 | 19.05×22 | 19.05×22
70 | Condenser Fin Pitch | mm | 1.4 | 1.4 | 1.4
71 | Condenser Fin Colour | － | blue | blue | blue
72 | Condenser Length(L) × Height(H) × Width(W) | mm | 851×660×38.1 | 851×660×38.1 | 982.2×748×38.1
73 | Condenser Max. Allowable Pressure | MPa | 10.0 | 10.0 | 10
74 | Permissible Excessive Operating Pressure for the Discharge Side | MPa | 4.3 | 4.3 | 4.3
75 | Permissible Excessive Operating Pressure for the Suction Side | MPa | 2.5 | 2.5 | 2.5
76 | Maximum Allowable Pressure | MPa | 4.3 | 4.3 | 4.3
77 | Cooling Operation Ambient Temperature Range | ℃ | -15~43 | -15~43 | 18～43
78 | Heating Operation Ambient Temperature Range | ℃ | -20～24 | -20～24 | -15～24
79 | Maximum drive IDU NO. | unit | 2 | 3 | 4
80 | Defrosting Method | -- | Automatic Defrosting | Automatic Defrosting | Automatic Defrosting
81 | Isolation | － | I | I | I
82 | Moisture Protection | -- | IP24 | IP24 | IP24
83 | Climate Type | － | T1 | T1 | T1
84 | Refrigerant | － | R410A | R410A | R410A
85 | Refrigerant Charge | kg | 1.6 | 2.2 | 2.4
86 | Throttling Method | － | Electron expansion valve | Electron expansion valve | Electron expansion valve
87 | Dimension of Outline(W×D×H) | mm | 955×396×700 | 955×396×700 | 980×427×790
88 | Dimension of Carton Box(L×W×H) | mm | 1026×455×735 | 1026×455×735 | 1080×485×840
89 | Dimension of Package(L×W×H) | mm | 1029×458×750 | 1029×458×750 | 1083×488×855
90 | Net Weight | kg | 51.0 | 62.0 | 69.0
91 | Gross Weight | kg | 55.5 | 66.5 | 74.0
92 | Outdoor Unit Loading Quantity ( 20’ Container ) | unit | 81 | 81 | 44
93 | Outdoor Unit Loading Quantity ( 40’ Container ) | unit | 171 | 171 | 96
94 | Outdoor Unit Loading Quantity ( 40’ High Cube Container ) | unit | 171 | 171 | 144
95 | Connection Pipe Connection Method | － | Flare Connection | Flare Connection | Flare Connection
96 | Not Additional Gas Connection Pipe Length | m | 10<Liquid pipe total length> | 30<Liquid pipe total length> | 40<Liquid pipe total length>
97 | Connection Pipe Gas Additional Charge | g/m | 20 | 20 | 20
98 | Connection Pipe Liquid Pipe Outer Diameter 1 | mm | φ6 | φ6 | φ6
99 | Connection Pipe Liquid Pipe Outer Diameter 2 | mm | φ6 | φ6 | φ6
100 | Connection Pipe Gas Pipe Outer Diameter 1 | mm | φ9.52 | φ9.52 | φ9.52
101 | Connection Pipe Gas Pipe Outer Diameter 2 | mm | φ9.52 | φ9.52 | φ9.52
102 | Connection Pipe Max. Height Distance(indoor and indoor) | m | 5 | 10 | 10
103 | Connection Pipe Max. Height Distance(indoor and outdoor and indoor up) | m | 5 | 10 | 10
104 | Connection Pipe Max. Height Distance(indoor and outdoor and outdoor up) | m | 5 | 10 | 10
105 | Max. equivalent connection pipe length(outdoor to last indoor) | m | 10 | 20 | 20
106 | Connection Pipe Max. Length Distance(total lenght) | m | 20 | 60 | 70